## 1 Coal supercritical
Technology
| Technology | Supercritical coal power plant
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 600 | 600 | 600 | 300 | 800 | 300 | 800 |  | 1
| Generating capacity for total power plant (MWe) | 1200 | 1200 | 1200 | 300 | 1800 | 300 | 1800 |  | 1
| Electricity efficiency, net (%), name plate | 37.6667 | 38.7967 | 39.9267 | 33 | 40 | 35 | 42 |  | 1;3;6;7
| Electricity efficiency, net (%), annual average | 36.6667 | 37.7667 | 38.8667 | 33 | 40 | 35 | 42 |  | 1;3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 3.75 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 2 | 4 | 4 | 1 | 4 | 3 | 4 | B | 1
| Minimum load (% of full load) | 50 | 25 | 20 | 25 | 75 | 10 | 30 | A | 1
| Warm start-up time (hours) | 6 | 4 | 4 | 2 | 8.5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 10 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2;4
| SO2 (degree of desulphuring, %) | 86 | 86 | 95 | 73 | 95 | 73 | 95 |  | 2;4
| NOX (g per GJ fuel) | 115 | 113 | 38 | 152 | 262.5 | 38 | 262.5 | C | 2;4
Financial data
| Nominal investment (M$/MWe) | 1.46 | 1.445 | 1.4243 | 0.72772 | 1.8193 | 0.72772 | 1.7101 | D;F;G | 1;3;6;7
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 39600 | 38500 | 37200 | 32100 | 53500 | 30100 | 50300 | F | 1;3;6;7
| Variable O&M ($/MWh) | 0.78 | 0.12101 | 0.11727 | 0.093564 | 1.0084 | 0.08795 | 0.14658 | F | 1;3
| Start-up costs ($/MWe/start-up) | 187 | 51.98 | 51.98 | 41.584 | 103.96 | 41.584 | 103.96 |  | 5
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IEA, World Energy Outlook, 2015.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability from 2030 to 2050.
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
D | For economy of scale a proportionality factor, a, of 0.8 is suggested.
E | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as +/- 25%.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 1 Coal ultra-supercrital
Technology
| Technology | Ultra-supercritical coal power plant
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 700 | 1200 | 700 | 1200 |  | 1
| Electricity efficiency, net (%), name plate | 42.5 | 43.775 | 45.05 | 40 | 45 | 42 | 47 |  | 1;3;6;7
| Electricity efficiency, net (%), annual average | 41.5 | 42.745 | 43.99 | 40 | 45 | 42 | 47 |  | 1;3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 4.3333 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 5 | 5 | 5 | 4 | 5 | 4 | 5 | B | 1
| Minimum load (% of full load) | 30 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1
| Warm start-up time (hours) | 4 | 4 | 4 | 2 | 5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 12 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 2;4
| SO2 (degree of desulphuring, %) | 86 | 86 | 95 | 73 | 95 | 73 | 95 |  | 2;4
| NOX (g per GJ fuel) | 152 | 150 | 38 | 152 | 262.5 | 38 | 262.5 | C | 2;4
Financial data
| Nominal investment (M$/MWe) | 1.632 | 1.6103 | 1.5995 | 0.86461 | 2.06 | 0.86461 | 1.9364 | D;F;G | 1;3;6;7
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 61100 | 59400 | 57500 | 46000 | 76500 | 43100 | 71800 | F | 1;3;6;7
| Variable O&M ($/MWh) | 0.11888 | 0.11532 | 0.11175 | 0.089163 | 0.14861 | 0.083814 | 0.13969 | F | 1;3
| Start-up costs ($/MWe/start-up) | 54.0384 | 54.0384 | 54.0384 | 43.2307 | 108.0768 | 43.2307 | 108.0768 |  | 5
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
3 | Learning curve approach for the development of financial parameters.
4 | Maximum emission from Minister of Environment Regulation 21/2008
5 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | IEA, World Energy Outlook, 2015.
Notes:
A | Assumed gradual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability from 2030 to 2050
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
D | For economy of scale a proportionality factor, a, of 0.8 is suggested.
E | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as +/- 25%.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 2 Coal CFB
Technology
| Technology | CFB boiler power plant ultra-supercritical
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref.
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 600 | 600 | 600 | 300 | 660 | 300 | 800 |  | 1;2
| Generating capacity for total power plant (MWe) | 1200 | 1200 | 1200 | 300 | 1200 | 300 | 1800 |  | 1
| Electricity efficiency, net (%), name plate | 41 | 42 | 43 | 37 | 43 | 39 | 45 |  | 1;2;3
| Electricity efficiency, net (%), annual average | 40 | 41 | 42 | 37 | 43 | 39 | 45 |  | 1;2;3
| Forced outage (%) | 7 | 6 | 3 | 5 | 15 | 2 | 7 | A | 1
| Planned outage (weeks per year) | 7 | 5 | 3 | 3 | 8 | 2 | 4 | A | 1
| Technical lifetime (years) | 30 | 30 | 30 | 25 | 40 | 25 | 40 |  | 1
| Construction time (years) | 3.75 | 3 | 3 | 3 | 5 | 2 | 4 | A | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configuration
| Ramping (% per minute) | 4 | 4 | 4 | 2 | 4 | 3 | 4 | B | 1,4
| Minimum load (% of full load) | 40 | 25 | 20 | 25 | 50 | 10 | 30 | A | 1,5
| Warm start-up time (hours) | 8 | 4 | 4 | 2 | 8.5 | 2 | 5 | B | 1
| Cold start-up time (hours) | 10 | 12 | 12 | 6 | 15 | 6 | 12 | B | 1
Environment
| PM 2.5 (mg per Nm3) | 70 | 70 | 70 | 50 | 150 | 20 | 100 | E | 3;6;7
| SO2 (degree of desulphuring, %) | 90 | 90 | 95 | 90 | 95 | 90 | 99 |  | 3;6;7
| NOX (g per GJ fuel) | 108 | 105 | 38 | 152 | 262.5 | 38 | 262.5 | C | 6;7;8
Financial data
| Nominal investment (M$/MWe) | 1.5282 | 1.5173 | 1.4955 | 0.72772 | 1.8193 | 0.72772 | 1.7101 | D;F;G | 1;7;9;10
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 40900 | 39800 | 38500 | 32100 | 53500 | 30100 | 50300 | F | 1;7;9;10
| Variable O&M ($/MWh) | 0.12475 | 0.12101 | 0.11727 | 0.093564 | 1.0084 | 0.08795 | 0.14658 | F | 1;7
| Start-up costs ($/MWe/start-up) | 51.98 | 51.98 | 51.98 | 41.584 | 103.96 | 41.584 | 103.96 |  | 12
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | IEA Clean Coal Centre, 2017, "The role of Circulating Fluidized Bed (CFB) Technology in Future Coal Power Generation"
3 | IEA Clean Coal Centre, 2013, "Techno-economic analysis of PC versus CFB combustion technology"
4 | Malgorzata Wiatros-Motyka, 2017, “The Lagisza Power Plant: The world’s First Supercritical CFB”, Link, Accessed 27th October 2020
5 | Prabir Basu, 2015, “Circulating Fluidized Bed Boilers. Design Operation and Maintenance”
6 | Platts Utility Data Institute (UDI) World Electric Power Plant Database (WEPP)
7 | Learning curve approach for the development of financial parameters.
8 | Fuel Processing technology, 2013, “Gas emissions from a large scale circulating fluidized bed boilers burning lignite and biomass”
9 | IEA, Projected Costs of Generating Electricity, 2015.
10 | IEA, World Energy Outlook, 2015.
11 | Research Fund for Coal & Steel, 2008, “Utility scale CFB for competitive coal power“
12 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Assumed no improvement for regulatory capability from 2030 to 2050
C | Calculated from a max of 750 mg/Nm3 to g/GJ (conversion factor 0.35 from Pollution Prevention and Abatement Handbook, 1998)
D | For economy of scale a proportionality factor, a, of 0.8 is suggested.
E | Uncertainty Upper is from regulation. Lower is from current standards in Japan (2020) and South Korea (2050).
F | Uncertainty (Upper/Lower) is estimated as +/- 25%.
G | Investment costs include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 3 SCGT
Technology
| Technology | Simple Cycle Gas Turbine - large system
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 50 | 50 | 50 | 35 | 65 | 35 | 65 |  | 3
| Generating capacity for total power plant (MWe) | 100 | 100 | 100 | 35 | 150 | 35 | 150 |  | 3
| Electricity efficiency, net (%), name plate | 33.5 | 36 | 40 | [5 empty] | 1;2
| Electricity efficiency, net (%), annual average | 32.5 | 35 | 39 | [5 empty] | 1;2
| Forced outage (%) | 2 | 2 | 2
| Planned outage (weeks per year) | 3 | 3 | 3
| Technical lifetime (years) | 25 | 25 | 25
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1.125 | 1.875 | 1.125 | 1.875 | B | 3
| Space requirement (1000 m2/MWe) | 0.02 | 0.02 | 0.02 | 0.015 | 0.025 | 0.015 | 0.025 | B | 3
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 | C | 3;8
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 | A | 6
| Warm start-up time (hours) | 0.25 | 0.23 | 0.2 | [5 empty] | 3
| Cold start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 7
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 86.4 | 60 | 20 | 20 | 86 | 20 | 86 | A;D | 3;7
Financial data
| Nominal investment (M$/MWe) | 0.61336 | 0.59257 | 0.56138 | 0.36386 | 1.2475 | 0.36386 | 0.83168 | F;G | 1-5
| - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| Fixed O&M ($/MWe/year) | 24100 | 23400 | 22700 | 18100 | 30100 | 17000 | 28400 | B | 1-5
Variable O&M ($/MWh)
| Start-up costs ($/MWe/start-up) | 24.9504 | 24.9504 | 24.9504 | 18.7128 | 31.188 | 18.7128 | 31.188 | B | 6
References:
1 | IEA, Projected Costs of Generating Electricity, 2015.
2 | IEA, World Energy Outlook, 2015.
3 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
4 | Learning curve approach for the development of financial parameters.
5 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
9 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
Notes:
A | Assumed gradidual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | The investment cost of an aero-derivative gas turbine will be in the higher end than an industrial gas turbine (ref. 5) . Roughly 50% higher.
G | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 3 CCGT
Technology
| Technology | Combined Cycle Gas Turbine
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 750 | 750 | 750 | 200 | 800 | 200 | 800 |  | 1
| Generating capacity for total power plant (MWe) | 1500 | 1500 | 1500 | 200 | 1600 | 200 | 1600 |  | 1
| Electricity efficiency, net (%), name plate | 56 | 60 | 61 | 45 | 62 | 55 | 65 |  | 1;3;5;10
| Electricity efficiency, net (%), annual average | 52 | 59 | 60 | 39 | 61 | 54 | 64
| Forced outage (%) | 5 | 5 | 5 | 3 | 10 | 3 | 10 |  | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | 3 | 8 | 3 | 8 |  | 1
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement (1000 m2/MWe) | - | - | - | - | - | - | -
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 7 | 20 | 20 | 10 | 30 | 10 | 30 | C | 1;2
| Minimum load (% of full load) | 56 | 30 | 15 | 30 | 50 | 10 | 40 | A | 5
| Warm start-up time (hours) | 2 | 1 | 1 | 1 | 3 | 0.5 | 2 | A | 1;5
| Cold start-up time (hours) | 3 | 2 | 2 | 2 | 5 | 2 | 5 |  | 1;5
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | E
| NOX (g per GJ fuel) | 78 | 60 | 20 | 20 | 86 | 20 | 86 | A;D | 7;8
Financial data
| Nominal investment (M$/MWe) | 0.76513 | 0.69 | 0.68 | 0.55 | 0.77 | 0.55 | 0.77 | F | 1;3;10
| - of which equipment (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| - of which installation (%) | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 9
| Fixed O&M ($/MWe/year) | 29350 | 28500 | 27600 | 22000 | 36700 | 20700 | 34500 | B | 1;3
| Variable O&M ($/MWh) | 0.45036 | 0.1261 | 0.1222 | 0.33777 | 0.56295 | 0.09165 | 0.15275 | B | 1
| Start-up costs ($/MWe/start-up) | 69.5115 | 70 | 70 | 52.1336 | 86.8894 | 52.5 | 87.5 | B | 6
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
3 | IEA, World Energy Outlook, 2015.
4 | Learning curve approach for the development of financial parameters.
5 | Siemens, 2010, "Flexible future for combined cycle".
6 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
7 | Maximum emission from Minister of Environment Regulation 21/2008
8 | Danish Energy Agency, 2015, "Technology Catalogue on Power and Heat Generation".
9 | Soares, 2008, "Gas Turbines: A Handbook of Air, Land and Sea Applications".
10 | IEA, Projected Costs of Generating Electricity, 2015.
Notes:
A | Assumed gradual improvement to international standard in 2050.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Assumed no improvement for regulatory capability.
D | Calculated from a max of 400 mg/Nm3 to g/GJ (conversion factor 0.27 from Pollution Prevention and Abatement Handbook, 1998)
E | Commercialised natural gas is practically sulphur free and produces virtually no sulphur dioxide
F | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 4 CCS coal supercritical
Technology
| Technology | Supercritical coal power plant with CCS - Retrofit post-combustion
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | -60 | -60 | -60 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | -60 | -60 | -60 |  |  |  |  | A | 1
| Electricity efficiency, net (%-point), name plate | -7 | -7 | -7 | [5 empty] | 1
| Electricity efficiency, net (%-point), annual average | -8 | -8 | -8 | [5 empty] | 1
| Forced outage (%-point) | 7 | 7 | 7
Planned outage (weeks per year)
Technical lifetime (years)
Construction time (years)
| CO2 emission reduction (%) | -88.76 | -90 | -90 |  |  | -90 | -99 | B | 1
Space requirement (1000 m2/MWe)
Ramping configuration
| Ramping (% per minute) | 4 | 4 | 4 |  |  |  |  | C | 7
| Minimum load (% of full load) | 30 | 30 | 30 |  |  |  |  | D | 7
| Warm start-up time (hours) | 4 | 4 | 4 |  |  |  |  | E | 8
| Cold start-up time (hours) | 12 | 12 | 12 |  |  |  |  | E | 8
Environment
| PM 2.5 (mg per Nm3) | 80.5 | 80.5 | 80.5 | [5 empty] | 3,7
| SO2 (degree of desulphuring, %) | 97 | 97 | 97 | [5 empty] | 3,7
| NOX (g per GJ fuel) | 115 | 113 | 38 | [5 empty] | 3,7
CH4 (g per GJ fuel)
N2O (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.0272 | 1.8609 | 1.4762 | 1.6634 | 2.3807 | 1.2163 | 1.7361 | F | 2,5,9,10
| - of which equipment (%) | 30 | 30 | 30 | 25 | 50 | 25 | 50 |  | 1
| - of which installation (%) | 70 | 70 | 70 | 50 | 75 | 50 | 75 |  | 1
| Fixed O&M ($/MWe/year) | 43500 | 42100 | 40900 | 13500 | 52000 | 13500 | 52000 | F | 1,7,9
| Variable O&M ($/MWh) | 3.2228 | 3.1292 | 3.0252 | 2.599 | 8.5247 | 2.4431 | 8.0153 | F | 1,5,9
References:
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | EIA, 2016, Capital Cost Estimates for Utility Scale Electricity Generating Plants
6 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermitent renewable energy sources
7 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2020
8 | IEAGHG, Operating Flexibility of Power Plants with CCS
9 | NREL ATB 2020
10 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020.
Notes:
A | The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.
F | Compression, transport and storage are not included in the figures

## 4 CCS CCGT
Technology
| Technology | Natural Gas Combined Cycle with CCS - Retrofit post-combustion
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | -40 | -40 | -40 |  |  |  |  | A | 1
| Generating capacity for total power plant (MWe) | -40 | -40 | -40 |  |  |  |  | A | 1
| Electricity efficiency, net (%), name plate | -7 | -7 | -7 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | -8 | -8 | -8 | [5 empty] | 1
| Forced outage (%) | 5 | 5 | 5
Planned outage (weeks per year)
| Technical lifetime (years) | -
Construction time (years)
| CO2 emission reduction (%) | -87.46 | -90 | -90 |  |  | -90 | -99 | B | 1
Space requirement (1000 m2/MWe)
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 |  |  |  |  | C | 6
| Minimum load (% of full load) | 45 | 45 | 45 |  |  |  |  | D | 6
| Warm start-up time (hours) | 2 | 2 | 2 |  |  |  |  | E | 4
| Cold start-up time (hours) | 4 | 4 | 4 |  |  |  |  | E | 4
Environment
| PM 2.5 (mg per Nm3) | 30 | 30 | 30 | [5 empty] | 3,6
| SO2 (degree of desulphuring, %) | 99 | 99 | 99 | [5 empty] | 3,6
| NOX (g per GJ fuel) | 78 | 60 | 20 | [5 empty] | 3,6
| CH4 (g per GJ fuel) | - | - | -
| N2O (g per GJ fuel) | - | - | -
Financial data
| Nominal investment (M$/MWe) | 1.1955 | 1.0084 | 0.7797 | 0.88366 | 1.6218 | 0.62376 | 1.0604 | F | 1,7,8
| - of which equipment (%) | 40 | 40 | 40 | 30 | 60 | 30 | 60 |  | 1
| - of which installation (%) | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 1
| Fixed O&M ($/MWe/year) | 9400 | 9000 | 8800 | 7300 | 14600 | 6900 | 14600 | F | 1,7,8
| Variable O&M ($/MWh) | 1.2475 | 1.2059 | 1.1747 | 0.62376 | 4.1584 | 0.62376 | 4.1584 | F | 1,7,8
References:
1 | Global CCS Institute, Global costs of carbon capture and storage, 2017
2 | Zero emissions platform, The Costs of CO2 Capture, Transport and Storage
3 | Koornneef J., 2011, Carbon Dioxide Capture and Air Quality
4 | IEAGHG, Operating Flexibility of Power Plants with CCS
5 | Utrecht University & Energy Research Center of Netherlands, The flexibility requirements for power plants with CCS in a future energy system with a large share of intermitent renewable energy sources
6 | Danish Energy Agency, "Technology data - Generation of electricity and district heating", 2020
7 | NREL ATB 2020
8 | IEA, Energy Technology Perspectives - Special Report on Carbon Capture, Utilisation and Storage, 2020.
Notes:
A | The difference in ouput power represents the additional power required by the auxiliary equipment (with CCS, ~10-15% of the net output).
B | This figure represents the efficiency of the capture process. New technologies might remove CO2 more efficiently in the future. CO2 can be already captured at higher rates, but costs to marginally increase capture rates beyond the reported values are relatively high.
C | In principle, ramping is not affected by the presence/absence of CCS.
D | Minimum load is not affected by CCS. However, the CO2 compressor requires higher loads for smooth operability.
E | The regeneration in the post-combustion unit has a start-up time comparable to that of the power plant.
F | Compression, transport and storage are not included in the figures

## 5 Cogeneration sugar
Biomass-fired co-generation in a sugar mill
| Technology | Biomass-fired cogeneration
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25 | 25 | 25 | 3.5 | 200 | 3.5 | 200 |  | 1;5;12
| Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1;5
| Electricity efficiency, net (%), name plate | 27 | 27 | 27 | 20 | 30 | 20 | 30 |  | 1;3;7
| Electricity efficiency, net (%), annual average | 26 | 26 | 26 | 20 | 30 | 20 | 30 | D | 1;3;7
| Total efficiency, net (%), name plate | 85 | 85 | 85 | 80 | 90 | 80 | 90 |  | 11
| Total efficiency, net (%), annual average | 84 | 84 | 84 | 80 | 90 | 80 | 90 |  | 11
| Forced outage (%) | 7 | 7 | 7 | 5.25 | 8.75 | 5.25 | 8.75 | A | 1
| Planned outage (weeks per year) | 26 | 26 | 26 | 24 | 28 | 24 | 28 | C | 1
| Technical lifetime (years) | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 | A | 8;7
| Construction time (years) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A | 7
| Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 | A | 1;9
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | [5 empty] | 3
| Minimum load (% of full load) | 30 | 30 | 30 | [5 empty] | 3
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
| Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 3
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3
Financial data
| Nominal investment (M$/MWe) | 1.7883 | 1.6452 | 1.4306 | 1.3412 | 2.2354 | 1.073 | 1.7883 | B | 4-8;10
| - of which equipment (%) | 65 | 65 | 65 | 50 | 85 | 50 | 85 |  | 1;2
| - of which installation (%) | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1;2
| Fixed O&M ($/MWe/year) | 49500 | 45500 | 39600 | 37100 | 61900 | 29700 | 49500 | A | 4;5;8;10
| Variable O&M ($/MWh) | 3.1638 | 2.9107 | 2.5311 | 2.3729 | 3.9548 | 1.8983 | 3.1638 | A | 5;10
Start-up costs ($/MWe/start-up)
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | ASEAN Centre of Energy, 2016, "Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states".
3 | Danish Energy Agency and COWI, 2017, "Technology catalogue for biomass to energy".
4 | IRENA, 2015, "Renewable power generation cost in 2014"
5 | IFC and BMF, 2017, "Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | India Central Electricity Authority, 2007, "Report on the Land Requirement of Thermal Power Stations".
10 | Learning curve approach for the development of financial parameters.
11 | Siemens, 2018: "The powerful potential of sugarcane"
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
C | Sugar production season is approximately half a year.
D | Power efficiency is reduced by 5 %-points compared to condensing operation to reflect steam extraction at higher temperature for process heat

## 5 Cogeneration cement
CHP in a cement factory
| Technology | CHP in a cement factory
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 8 | 8 | 8 | 2 | 20 | 2 | 20 |  | 1,2,3
Generating capacity for total power plant (MWe)
| Electricity efficiency, net (%), name plate | 18 | 18 | 18 | 15 | 25 | 15 | 25 |  | 3
Electricity efficiency, net (%), annual average
Forced outage (%)
Planned outage (weeks per year)
Technical lifetime (years)
Construction time (years)
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
Capacity factor (%), theoretical
Capacity factor (%), incl. outages
Ramping configuration
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |  | 4
| - of which equipment (%) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | A
| - of which installation (%) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | A
Fixed O&M ($/MWe/year)
| Variable O&M ($/MWh) | 12.5 | 12.5 | 12.5 | 5 | 20 | 5 | 20 |  | 2
Start-up costs ($/MWe/start-up)
References:
1 | Khurana, S., Banerjee, J., & Gaitonde, U. (2006). Energy balance and cogeneration for a cement plant. Appl. Therm. Eng., 2479-2489.
2 | Irungu, S. N., & Muchiri, P. &. (2017). The generation of power from a cement kiln waste gases: a case study of a plant in Kenya. Energy Science & Engineering, 90-99
3 | Paredes-Sánchez, J. P. (2015). Using waste energy from the Organic Rankine Cycle cogeneration in the Portland cement industry. DYNA, 15-20.
4 | Institute for Industrial Productivity. (2014). Waste Heat Recovery for the Cement Sector: Market and Supplier Analysis.
Notes:
A | Own estimate.
Note on C29: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: C29-I30 revised to % instead of M$/MWe

## 6 Small hydro
Technology
| Technology | Hydro power plant - Small system
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 30 | 30 | 30 | 1 | 30 | 1 | 30 |  | 2
| Generating capacity for total power plant (MWe) | 30 | 30 | 30 | 1 | 30 | 1 | 30 |  | 2
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 1
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | 10.5 | 17.5 | 10.5 | 17.5 | B
Additional data for non thermal plants
| Capacity factor (%), theoretical | 80 | 80 | 80 | 50 | 95 | 50 | 95 |  | 8;9
| Capacity factor (%), incl. outages | 75.8846 | 75.8846 | 75.8846 | 50 | 95 | 50 | 95 |  | 8;9
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$19/MWe) | 1.75 | 1.75 | 1.75 | 0.8 | 4 | 0.8 | 4 | C;D | 4;5;6;7
| - of which equipment (%) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 7
| - of which installation (%) | 70 | 70 | 70 | 50 | 80 | 50 | 80 |  | 7
| Fixed O&M ($/MWe/year) | 41900 | 39800 | 37300 | 22000 | 41900 | 22000 | 41900 |  | 4;5;7
| Variable O&M ($19/MWh) | 0.5 | 0.475 | 0.445 | 0.375 | 0.625 | 0.33375 | 0.55625 | B | 1
| Start-up costs ($19/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
Size of reservoir (MWh)
References:
1 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
2 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
5 | IEA, World Energy Outlook, 2015.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
8 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
9 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 6 Large hydro
Technology
| Technology | Hydro power plant - large system
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 150 | 150 | 150 | 30 | 2000 | 30 | 2000 |  | 1;8;10
| Generating capacity for total power plant (MWe) | 150 | 150 | 150 | 30 | 2000 | 30 | 2000 |  | 1;8;10
| Electricity efficiency, net (%), name plate | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Electricity efficiency, net (%), annual average | 95 | 95 | 95 | 85 | 97 | 85 | 97 | A | 7
| Forced outage (%) | 4 | 4 | 4 | 2 | 10 | 2 | 10 |  | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 3 | 10 | 3 | 10 |  | 1
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 | B | 1
| Construction time (years) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Space requirement (1000 m2/MWe) | 62 | 62 | 62 | 46.5 | 77.5 | 46.5 | 77.5 | C | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 40 | 40 | 40 | 20 | 95 | 20 | 95 |  | 2;12
| Capacity factor (%), incl. outages | 35.8846 | 35.8846 | 35.8846 | 20 | 95 | 20 | 95 |  | 2;12
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 |  | 3
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 3
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$19/MWe) | 1.5 | 1.5 | 1.5 | 0.6 | 8 | 0.6 | 8 | D;E | 1;4;5;6;9
| - of which equipment (%) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 11
| - of which installation (%) | 70 | 70 | 70 | 50 | 80 | 50 | 80 |  | 11
| Fixed O&M ($/MWe/year) | 37700 | 35800 | 33600 | 28300 | 47100 | 25200 | 42000 | C | 1;4;5;6
| Variable O&M ($19/MWh) | 0.65 | 0.6175 | 0.5785 | 0.4875 | 0.8125 | 0.43388 | 0.72313 | C | 1;5
| Start-up costs ($19/MWe/start-up) | - | - | - | - | - | - | -
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Branche, 2011, “Hydropower: the strongest performer in the CDM process, reflecting high quality of hydro in comparison to other renewable energy sources”.
3 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
4 | IEA, World Energy Outlook, 2015.
5 | Learning curve approach for the development of financial parameters.
6 | IEA, Projected Costs of Generating Electricity, 2015.
7 | Stepan, 2011, Workshop on Rehabilitation of Hydropower, “The 3-Phase Approach”.
8 | Prayogo, 2003, "Teknologi Mikrohidro dalam Pemanfaatan Sumber Daya Air untuk Menunjang Pembangunan Pedesaan. Semiloka Produk-produk Penelitian Departement Kimpraswill Makassar".
9 | Energy and Environmental Economics, 2014, "Capital Cost Review of Power Generation Technologies - Recommendations for WECC’s 10- and 20-Year Studies".
10 | General Electric, www.gerenewableenergy.com, Accessed: 20th July 2017
11 | ASEAN, 2016, "Levelised cost of electricity of selected renewable technologies in the ASEAN member states".
12 | MEMR, 2016, "Handbook of Energy & Economic Statistics of Indonesia 2016", Ministry of Energy and Mineral Resources, Jakarta, Indonesia.
Notes:
A | This is the efficiency of the utilization of the waters potential energy. This can not be compared with a thermal power plant that have to pay for its fuel.
B | Hydro power plants can have a very long lifetime is operated and mainted properbly. Hover Dam in USA is almost 100 years old.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 7 Ground-mounted PV
Technology
| Technology | Utility-scale Solar PV
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity a typical power plant (MWe) | 50 | 50 | 50 |  |  |  |  | C | 1
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 35 | 40 | 40 | 25 | 40 | 35 | 45 |  | 1,6
| Construction time (years) | 0.7 | 0.5 | 0.5 | 0.3 | 1 | 0.25 | 1 |  | 5
| Space requirement (1000 m2/MWp) | 10.5 | 10.5 | 10.5 | 10 | 11 | 10 | 11 |  | 5
Additional data for non thermal plants
| Capacity factor (%), theoretical | 21 | 24 | 24 | 14 | 23 | 14 | 24 |  | 1,2
| Capacity factor (%), incl. outages | 21 | 24 | 24 | 14 | 23 | 14 | 24 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 0.93 | 0.66 | 0.48 | 0.87 | 0.97 | 0.31 | 0.71 | D,R,S | 1,3,4,5
| - of which equipment | 38.71% | 36.35% | 24.81%
| - of which installation | 61.29% | 63.65% | 75.19%
| Fixed O&M ($/MWe/year) | 15500 | 10000 | 8000 | 11600 | 19400 | 5300 | 10700 | E,Q | 1,6
| Variable O&M ($/MWh) | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1600 | 1600 | 1600 | 1200 | 1900 | 1200 | 1900 | F | 8
| DC/AC sizing factor (Wp/W) | 1.2 | 1.2 | 1.2 |  |  |  |  | G | 5
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
| Performance ratio [-] | 0.84 | 0.87 | 0.9 |  |  |  |  | I | 5.6
| PV module conversion efficiency (%) | 20% | 23% | 26% | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kW) | 1600 | 1700 | 1750 |  |  |  |  | J, L, T
| Peak power full load hours (kWh/kWp) | 1350 | 1400 | 1450 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.3 | 0.2 | 0.1 | [5 empty] | 6.9
| Balance Of Plant cost ($/Wp) | 0.475 | 0.35025 | 0.303 | [5 empty] | 6.9
| Specific investment, total system ($/Wp) | 0.775 | 0.55025 | 0.403 |  |  |  |  | M | 5,6,9
| Specific investment, total system (M$/MW) | 0.93 | 0.6603 | 0.4836 |  |  |  |  | P
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2020, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Data analysed from www.renewables.ninja for multiple locations.
3 | IEA, World Energy Outlook, 2019.
4 | Learning curve approach for the development of financial parameters.
5 | Local cases data
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | ENF Solar, directory of solar companies and products
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location. Here the main value is taken based on a good location for a solar project, and the range is represented as an uncertainty.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Vietnamese prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
T | Full load hours: Total hours in a year where the plant produces power at rated capacity.

## 7 Rooftop PV
Technology
| Technology | Rooftop PV grid connected
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for total power plant (kW) | 10 | 10 | 10 |  |  |  |  | C | 1,5,6
| Electricity efficiency, net (%), name plate | - | - | - |  |  |  |  | A
| Electricity efficiency, net (%), annual average | - | - | - |  |  |  |  | A
| Forced outage (%) | - | - | -
| Planned outage (weeks per year) | - | - | -
| Technical lifetime (years) | 35 | 40 | 40 | 25 | 40 | 35 | 45 |  | 1,6
| Construction time (years) | 0.04 | 0.04 | 0.04 | 0.01 | 0.13 | 0.01 | 0.13 |  | 5
| Space requirement (m2/kW) | 6.5 | 6 | 5 | 4.875 | 8.125 | 5 | 6.25 |  | 1,5
Additional data for non thermal plants
| Capacity factor (%), theoretical | 15.9817 | 16.5525 | 17.1233 | 14 | 23 | 14 | 24 |  | 1,2
| Capacity factor (%), incl. outages | 15.9817 | 16.5525 | 17.1233 | 14 | 23 | 14 | 24 |  | 1,2
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | - | B
| Cold start-up time (hours) | - | - | - | - | - | - | - | B
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1 | 0.71 | 0.52 | 1.45 | 1.6 | 0.5 | 1.2 | D,R,S | 3,4,5
| - of which equipment | 40.4% | 40% | 39.22%
| - of which installation | 59.6% | 60% | 60.78%
| Fixed O&M ($/MWe/year) | 14800 | 10000 | 8000 | 11100 | 18500 | 5300 | 10700 | E,Q | 6
| Variable O&M ($/MWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology specific data
| Global horizontal irradiance (kWh/m2/y) | 1600 | 1600 | 1600 | 1200 | 1900 | 1200 | 1900 | F | 8
| DC/AC sizing factor (Wp/W) | 1.05 | 1.05 | 1.05 |  |  |  |  | G | 5
| Transposition Factor for fixed tilt system | 1.01 | 1.01 | 1.01 |  |  |  |  | H | 8
| Performance ratio | 0.84 | 0.87 | 0.9 |  |  |  |  | I | 5.6
| PV module conversion efficiency (%) | 20% | 23% | 26% | [5 empty] | 6
| Inverter lifetime (years) | 15 | 15 | 15 | [5 empty] | 6
Output
| Full load hours (kWh/kW) | 1400 | 1450 | 1500 |  |  |  |  | J, L, T
| Peak power full load hours (kWh/kWp) | 1350 | 1400 | 1450 |  |  |  |  | K, L
Financial data
| PV module & inverter cost ($/Wp) | 0.4 | 0.28 | 0.2 | [5 empty] | 6.9
| Balance Of Plant cost ($/Wp) | 0.8 | 0.559 | 0.47467 | [5 empty] | 6.9
| Specific investment, total system ($/Wp) | 0.99 | 0.7 | 0.51 |  |  |  |  | M | 5,6,9
| Specific investment, total system (million $/MW) | 1.0395 | 0.735 | 0.5355 |  |  |  |  | P
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2020, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Data analysed from www.renewables.ninja for multiple locations.
3 | IEA, World Energy Outlook, 2019.
4 | Learning curve approach for the development of financial parameters.
5 | Local cases data
6 | The Danish Energy Agency, Generation of electricity and district heating, 2020.
7 | Permasalahan penetrasi solar pv pada sistem grid nasional, Dewan Energi Nasional, Juni 2017 PT Len Industri (Persero)
8 | PVGIS © Europeen Communitees 2001-2012.
9 | Learning curve based forecast of technology costs. Ea Energy Analyses, 2020
Notes:
A | See "PV module conversion efficiency (%)". The improvement in technology development is also captured in capacity factor, investment costs and space requirement.
B | The production from a PV system reflects the yearly and daily variation in solar irradiation. It is possible to curtail solar, and this can be done rapidly.
C | Listed as MWe. The MWp will be around 10% higher.
D | Assumptions described in the section "Assumptions and perspectives for further development"
E | Uncertainty (Upper/Lower) is estimated as +/- 25%.
F | The global horizontal irradiation is a measure of the energy resource potential available and depends on the exact geographical location.
G | The DC/AC shown in the table equals module peak capacity divided by plant capacity. The sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity.
H | The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. In Indonesia the TF factor for fixed systems is very low, adding only 0-1 % to the production.
I | The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non- STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
J | The number of full load hours is calculated based on the other values in the table. The formula is: Full load hours = Global horizontal irradiance * transposition factor * performance ratio.
K | Also known as the specific yearly energy production (kWh/kWp) of the PV modules. This value is calculated from this formula: Peak power full load hours = 1046 * transposition factor * (1-incident angle modifier loss) * (1-PV system losses etc.) * (1-inverter loss) * (1-AC grid loss).
L | Capacity factor = Full load hours / 8760.
M | Current international market prices for utility scale PV systems have been estimated based on interviews with Danish developers and an assesment of the prices from Danish and Germany tenders for PV capacity in 2016 and the beginning of 2017. The forecasted internatinal price is based on estimated learning rates for the module and invester (20 % learning rate) and balance of plant (10 % learning rate) and a projection of the cumulated PV capacity based on the IEA's 450 ppm scenario. The share that the PV module and the invester accounts for decreases over time as the result of the higher learning rate compared to the balance of plant. Viatnamese prices are assumed to be somewhat higher in the first years thereafter approaching gradually the international level.
P | The “specific investment, total system per rated capacity W(AC)” is calculated as “specific investment, total system per Wp(DC)” multiplied by the sizing factor.
Q | The cost of O&M includes insurance and regular replacement of inverters and land-lease. Annual O&M is estimated to be 2 % of investment cost per MWp.
R | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.
S | For 2020, uncertainty ranges are based on cost spans of various sources. For 2050, we combine the base uncertainity in 2020 with an additional uncertainty span based on learning rates variying between 17.5-22.5% and capacity deployment from Stated Policies and Sustainable Development scenarios separately.
T | Full load hours: Total hours in a year where the plant produces power at rated capacity.

## 8 Wind onshore
Technology
| Technology | Wind power - Onshore - Low-wind turbines
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 3.5 | 4.5 | 5.2 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 30 | 80 | 100 | [5 empty] | 1
| Electricity efficiency, net (%), name plate | [7 empty] | A
Electricity efficiency, net (%), annual average
| Forced outage (%) | 2.5 | 2 | 2
| Planned outage (weeks per year) | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 |  | 3
| Technical lifetime (years) | 27 | 30 | 30 | 25 | 35 | 25 | 40 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 14 | 14 | 14 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 35 | 35.56 | 36.68 | 20 | 45 | 20 | 45
| Capacity factor (%), incl. outages | 34.02 | 34.7416 | 35.8358
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | D
| Minimum load (% of full load) | - | - | - | - | - | - | - | D
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 1.5 | 1.28 | 1.08 | 1.4 | 2.0 | 1.0 | 1.5 | C | 1, 3
| - of which equipment (%) | 65 | 65 | 65 |  |  |  |  | B | 2, 3
| - of which installation (%) | 35 | 35 | 35 |  |  |  |  | B | 2, 3
| Fixed O&M ($/MWe/year) | 42000 | 36000 | 28000 | 36500 | 44600 | 28700 | 43100 |  | 1, 3
| Variable O&M ($/MWh) | 3.5 | 2.8 | 2.3 | 3.2 | 4 | 2 | 3 |  | 3
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 135 | 155 | 170 | 90 | 130 | 100 | 150 |  | 3, 4
| Hub height (m) | 130 | 150 | 170 | 85 | 120 | 85 | 150 |  | 3, 4
| Specific power (W/m2) | 244.5179 | 238.484 | 229.095 | 270 | 350 | 250 | 350 |  | 3, 4
| Availability (%) | 96.38% | 96.88% | 96.88% | 95 | 99 | 95 | 99 |  | 3, 4
References:
1 | Ea Energy Analyses and Danish Energy Agency, Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity, 2020
2 | IRENA (2015). Renewable Power Generation Cost in 2014
3 | Danish Energy Agency, Technology Data - Generation of Electricity and District Heating, 2020.
4 | IEA Wind Task 26, International Technology Catalogue for Wind Power, 2021.
Notes:
A | The efficiency is defined as 100%. The improvement in technology development is captured in capacity factor, investment cost and space requirement.
B | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
C | Projections based on the learning rate approach
D | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).

## 8 Wind offshore Nearshore
Technology
| Technology | Wind power - Nearshore
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 4 | 5.5 | 6 | 2.5 | 6 | 4 | 20 |  | 1, 2
| Generating capacity for total power plant (MWe) | 50 | 100 | 200 | 50 | 500 | 50 | 3000 | D | 1
Electricity efficiency, net (%), name plate
Electricity efficiency, net (%), annual average
| Forced outage (%) | 4 | 3 | 3 | 1 | 5 | 1 | 5 | E | 1
| Planned outage (%) | 0.3 | 0.3 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | E | 1
| Technical lifetime (years) | 25 | 30 | 30 | 20 | 35 | 20 | 35 | E | 1
| Construction time (years) | 2.5 | 2 | 2 | 1.5 | 4 | 1.5 | 4 | E | 1
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | 168 | 204 | 168 | 204 | E | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 43% | 48% | 55% | - | - | - | -
| Capacity factor (%), incl. outages | 41.15% | 46.42% | 53.19% | - | - | - | -
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 2 | 1.5 | 1.3 | 1.5 | 3 | 1 | 2 | C | 1,4,6
| - of which equipment (%) | 45 | 50 | 50 | 40 | 50 | 40 | 50 | A | 1,4,6
| - of which installation (%) | 55 | 50 | 50 | 50 | 60 | 50 | 60 | A | 1,4,6
| Fixed O&M ($/MWe/year) | 55000 | 40000 | 32000 | 40000 | 100000 | 25000 | 45000 |  | 1, 3, 4,6
| Variable O&M ($/MWh) | 4.5 | 3 | 2.5 | 3 | 5 | 2 | 3 |  | 1, 3, 4,6
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 140 | 170 | 180 | [5 empty] | 1,5
| Hub height (m) | 110 | 150 | 175 | [5 empty] | 1,5
| Specific power (W(m2) | 259.8448 | 242.312 | 235.7851 | [5 empty] | 1,5
| Availability (%) | 97.5% | 98% | 98% | 95 | 99 | 95 | 99 |  | 1,5
References:
1 | 4C Offshore project database.
2 | IRENA, Future of Wind, 2019.
3 | IEA Wind Task 26, Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2012–2018, 2019
4 | AEGIR, Vietnam site LCOE screening, 2020.
5 | IEA Wind Task 26, International technology catalogue for wind energy, 2020 (draft report).
6 | Zhang S. Et al., Economy Comparison of Intertidal Zone Wind Farm and Normal Offshore Wind Farm, IEEE, 2011.
Notes:
A | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
B | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
C | The AEGIR report and the Danish TC (ref. 1 and 4 above) have been used to calculate best estimates for Vietnam.
D | The wind farm size is indicative and can vary greatly from site to site. In broad terms, the average size of offshore farms increases with distance from shore due to the impact assessment.
E | There is no substantial difference between intertidal and offshore wind outage and lifetime. However, towing is a less lengthy process.

## Nearshore investment cost (hidden)
No. | Nearshore wind projects | Province | Capacity (MW) | Period | Investment cost (M$/MW)
1 | Dong Hai 5 | Bac Lieu | 350 | 2021-2025 | 1.97
2 | Trung Nam - Tra Vinh (V3-6) | Tra Vinh | 348 | 2021-2025 | 1.91
3 | Marshal Ben Tre | Ben Tre | 125 | 2021-2025 | 1.8
4 | Ca Mau 2 | Ca Mau | 2000 | 2021-2025 | 1.78
5 | Vinh Hai | Soc Trang | 800 | 2021-2025 | 2.16
6 | Dong Hai 5.1 | Bac Lieu | 800 | 2021-2025 | 2.51
7 | Phu Cuong Soc Trang 2 | Soc Trang | 1000 | 2026-2030 | 2.25
8 | V1-2 Extend | Tra Vinh | 48 | 2021-2025 | 1.95
| Average |  |  |  | 2.0413

## 8 Wind offshore fixed
Technology
| Technology | Wind power - Offshore
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 5.7 | 10 | 14 | 1.6 | 15 | 4 | 20 |  | 1, 2
| Generating capacity for total power plant (MWe) | 100 | 500 | 1000 | 50 | 500 | 50 | 3000 | D | 1
Electricity efficiency, net (%), name plate
Electricity efficiency, net (%), annual average
| Forced outage (%) | 4 | 3 | 3 | 1 | 5 | 1 | 5 |  | 1
| Planned outage (%) | 0.3 | 0.3 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 |  | 1
| Technical lifetime (years) | 25 | 30 | 30 | 20 | 35 | 20 | 35 |  | 1
| Construction time (years) | 3 | 2.5 | 2.5 | 1.5 | 4 | 1.5 | 4 |  | 1
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | 168 | 204 | 168 | 204 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 43% | 48% | 55% | - | - | - | -
| Capacity factor (%), incl. outages | 41.15% | 46.42% | 53.19% | - | - | - | -
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 3.15 | 2.15 | 1.7 | 2 | 3.5 | 1.4 | 2 | C | 1,4
| - of which equipment (%) | 45 | 50 | 50 | 40 | 50 | 40 | 50 | A | 1,4
| - of which installation (%) | 55 | 50 | 50 | 50 | 60 | 50 | 60 | A | 1,4
| Fixed O&M ($/MWe/year) | 70000 | 42000 | 39000 | 40000 | 100000 | 25000 | 45000 |  | 1, 3, 4
| Variable O&M ($/MWh) | 5 | 3.051 | 2.7 | 3 | 3.7 | 2 | 3 |  | 1, 3, 4
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 150 | 200 | 240 | [5 empty] | 1
| Hub height (m) | 130 | 170 | 190 | [5 empty] | 1
| Specific power (W(m2) | 322.554 | 318.3099 | 309.4679 | [5 empty] | 1
| Availability (%) | 97% | 97.5% | 97.5% | 95 | 99 | 95 | 99 |  | 1
References:
1 | Danish Energy Agency, Technology Data on Energy Plants - Generation of Electricity and District Heat, 2020.
2 | IRENA, Future of Wind, 2019.
3 | IEA Wind Task 26, Wind Technology, Cost, and Performance Trends in Denmark, Germany, Ireland, Norway, the EU, and the USA: 2012–2018, 2019
4 | AEGIR, Vietnam site LCOE screening, 2020.
Notes:
A | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
B | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
C | The AEGIR report and the Danish TC (ref. 1 and 4 above) have been used to calculate best estimates for Vietnam.
D | The wind farm size is indicative and can vary greatly from site to site

## 8 Wind offshore floating
Technology
| Technology | Wind power - Floating offshore
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 7 | 12 | 15 | [5 empty] | 1, 2, 5
| Generating capacity for total wind farm (MWe) | 35 | 500 | 1000 | [5 empty] | 1, 5
Electricity efficiency, net (%), name plate
Electricity efficiency, net (%), annual average
| Forced outage (%) | 6 | 4 | 4 | [5 empty] | 3
| Planned outage (%) | 0.6 | 0.6 | 0.6 | [5 empty] | 3
| Technical lifetime (years) | 20 | 25 | 30 | [5 empty] | 4
| Construction time (years) | 3 | 2.5 | 2.5 | [5 empty] | 4
| Space requirement (1000 m2/MWe) | 185 | 185 | 185 | [5 empty] | 4
Additional data for non thermal plants
| Capacity factor (%), theoretical | 43% | 48% | 55% | - | - | - | - | D
| Capacity factor (%), incl. outages | 40.16% | 45.79% | 52.47% | - | - | - | -
Ramping configurations
| Ramping (% per minute) | - | - | - | - | - | - | - | B
| Minimum load (% of full load) | - | - | - | - | - | - | - | B
| Warm start-up time (hours) | - | - | - | - | - | - | -
| Cold start-up time (hours) | - | - | - | - | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | -
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.5 | 2.65 | 2 | 4 | 7 | 1.5 | 2.5 |  | 3,4,5
| - of which equipment (%) | 80 | 65 | 60 |  |  |  |  | A
| - of which installation (%) | 20 | 35 | 40 |  |  |  |  | A
| Fixed O&M ($/MWe/year) | 155000 | 125000 | 65000 | 140000 | 180000 | 52000 | 81000 | C | 4; 5; 6
| Variable O&M ($/MWh) | - | - | - |  |  |  |  | C | 4; 5
| Start-up costs ($/MWe/start-up) | 0 | 0 | 0
Technology specific data
| Rotor diameter (m) | 150 | 200 | 250 | [5 empty] | 1
| Hub height (m) | 100 | 170 | 180 | [5 empty] | 1
| Specific power (W/m2) | 396.119 | 381.9719 | 305.5775 | [5 empty] | 1
| Availability (%) | 94% | 96% | 96% | [5 empty] | 3
References:
1 | Global Wind Energy Council, 2020, "Global Offshore Wind Report 2020"
2 | BVG Associates, 2020, "Offshore wind roadmap for Vietnam"
3 | Borg M. et al., Qualification of innovative floating substructures for 10MW wind turbines and water depths greater than 50m, 2019
4 | World Bank, Offshore wind roadmap for Vietnam: Preliminary Findings, 2020.
5 | AEGIR, Vietnam site LCOE screening, 2020.
6 | M. Aquilina, 2014, "Cost Modelling of Floating Wind Farms with Upscaled Rotors in Maltese Waters"
Notes:
A | Equipment: Cost of turbines including transportation. Installation: Electricical infrastructure of turbine, civil works, grid connection, planning and management. The split of cost may vary considerably from project to project.
B | With sufficient wind resource available (wind speed higher than 4-6 m/s and lower than 25-30 m/s) wind turbines can always provide down regulation, and in many cases also up regulation, provided the turbine is running in power-curtailed mode (i.e. with an output which is deliberately set below the possible power based on the available wind).
C | Operation and maintenance is entirely allotted to the fixed part
D | In Vietnam, floating offshore sites - further from shore - have the same average wind speeds as fixed-bottom sites

## 9 Tidal power impoundment
Technology
| Technology | Tidal power - Impoundment Type
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 10 | 25 | 1 | 25 | 1 | 25 | A | 3
| Generating capacity for total power plant (MWe) | 30 | 100 | 150 | 10 | 300 | 10 | 300 | B | 3
| Electricity efficiency, net (%), name plate | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
| Electricity efficiency, net (%), annual average | 90 | 90 | 90 | 85 | 95 | 85 | 95 | F | 5
| Forced outage (%) | 4% | 4% | 4% | 2% | 6% | 2% | 6%
Planned outage (weeks per year)
| Technical lifetime (years) | 40 | 40 | 50 | 30 | 120 | 30 | 120 | C | 2
| Construction time (years) | 5 | 5 | 4 | 4 | 6 | 4 | 6 |  | 3,5
| Space requirement (1000 m2/MWe) | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | D
Additional data for non thermal plants
| Capacity factor (%), theoretical | 35 | 35 | 40 | 35 | 40 | 35 | 40 | E
Capacity factor (%), incl. outages
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 30 | 100 | 30 | 100 | G
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 | G
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.5 | 5.1092 | 5.1 | 2.9 | 7.5 | 2.9 | 7.5 | E | 1,2,4
- of which equipment
- of which installation
| Fixed O&M ($/MWe/year) | 70800 | 62500 | 35700 | 23400 | 72000 | 23400 | 72000 | E | 1,2,3,4
| Variable O&M ($/MWh) | 0 | 0 | 0
Start-up costs ($/MWe/start-up)
Technology specific data
References:
1 | DECC GOV.UK, “The UK 2050 Calculator: Tidal Range Cost Data,” 2011.
2 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010
3 | IRENA, “Tidal Energy Technology Brief,” 2014
4 | Pacific Northwest National Laboratory (PNNL), Tethys
5 | Tatiana Montllonch Araquistain, Tidal Power: Economic and Technological assessment.
Notes:
A | Based on various projects and company datasheets. The turbine size can vary from project to project based on requirement. The Sihwa Lake project in Korea has 25.4 MW turbines.
B | The capacity is strongly dependent on resources available and shape of coastline. Although a lot of proposed plants are much larger in size, with some being over 2 GW as well, the capacity shown here is based on deployment of plants so far.
C | Actual operational life can be upto 120 years. However, lifetime is taken as 40 years, since there can be significant re-fitting costs after 40 years and discounted cash flows are insignificant after 40 years.
D | Based on information of proposed plants.
E | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
F | Bulb type turbines are commonly used for tidal impoundment plants. The value here is estimated based on efficiencies of bulb type water turbines.
G | Considered as similar to Hydro

## 9 Tidal power stream
Technology
| Technology | Tidal power - Stream Type
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 2 | 2 | 0.1 | 6 | 1 | 6 | A | 3,5
| Generating capacity for total power plant (MWe) | 10 | 150 | 150 | 1 | 400 | 1 | 400 | A | 3,5
| Electricity efficiency, net (%), name plate | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2,3,5
| Electricity efficiency, net (%), annual average | 90 | 92 | 95 | 87 | 97 | 87 | 97 | B | 2,3,5
| Forced outage (%) | 4% | 4% | 4% | 2% | 6% | 2% | 6% |  | 2
Planned outage (weeks per year)
| Technical lifetime (years) | 25 | 25 | 30 | 20 | 30 | 20 | 30 | B
| Construction time (years) | 3 | 2 | 2 |  |  |  |  | C
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1,2,4
| Capacity factor (%), incl. outages | 33 | 35 | 37 | 33 | 40 | 35 | 40 | B | 1,2,4
Ramping configurations
| Ramping (% per minute) | - | - | -
| Minimum load (% of full load) | - | - | -
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 5.7 | 4.6 | 3.4 | 3 | 7.1 | 2 | 7.1 | B | 1,2,3
| - of which equipment (%) | 87 | 87 | 87 | 83 | 91 | 83 | 91 |  | 1,2
| - of which installation (%) | 13 | 13 | 13 | 9 | 17 | 9 | 17 |  | 1,2
| Fixed O&M ($/MWe/year) | 283622.0434 | 230297.5991 | 114717.9303 | 92700 | 412000 | 92700 | 412000 | B | 1,2
| Variable O&M ($/MWh) | 11.7257 | 8.7943 | 7.3286 | [5 empty] | 4
Start-up costs ($/MWe/start-up)
Technology specific data
References:
1 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010.
2 | Ocean Energy Systems - OES (IEA), “International Levelised Cost of Energy for Ocean Energy Technologies,” 2015.
3 | SIMEC Atlantis Energy, Projects
4 | UK Govt., Electricity Generation Costs 2020 (back calculation from LCOE values)
5 | Pacific Northwest National Laboratory (PNNL), Tethys
Notes:
A | Projects are in the early stages os turbines and capacities are smaller. Larger projects are expected to be executed in smaller capacity phases.
B | The projections here are assuming that with increased deployment and improved technology the values will improve within the range estimated.
C | Estimated based on MeyGen tidal stream project
Note on B31: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: % signs incl
Note on I32: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: changed to numbers

## 10 Wave power
Technology
| Technology | Wave power
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 0.2 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.5 | A | 4
| Generating capacity for total power plant (MWe) | <1 | 5 | 25 | <1 | 3 | 2 | 75 | B | 1,4
| Electricity efficiency, net (%), name plate | 80% | 80% | 80% | 55% | 95% | 55% | 95% | C | 3
| Electricity efficiency, net (%), annual average | 80% | 80% | 80% | 55% | 95% | 55% | 95% | C | 3
| Forced outage (%) | 10% | 8% | 4% | 2% | 15% | 2% | 5% |  | 1,2
Planned outage (weeks per year)
| Technical lifetime (years) | 10 | 15 | 25 | 5 | 15 | 20 | 30 |  | 4
| Construction time (years) | 3 | 3 | 3 | 2 | 4 | 2 | 4 |  | 4
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | 30% | 32% | 38% | 20% | 40% | 30% | 45% | A | 1,2,3
| Capacity factor (%), incl. outages | 30% | 32% | 38% | 20% | 40% | 30% | 45% | A | 1,2,3
Ramping configurations
| Ramping (% per minute) | - | - | -
| Minimum load (% of full load) | - | - | -
| Warm start-up time (hours) | - | - | -
| Cold start-up time (hours) | - | - | -
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0
| CH4 (g per GJ fuel) | 0 | 0 | 0
| N2O (g per GJ fuel) | 0 | 0 | 0
Financial data
| Nominal investment (M$/MWe) | 10.75 | 8.55 | 5.45 | 4.1 | 18.6 | 2.7 | 9.3 |  | 1,5,7
| - of which equipment (%) | 87 | 87 | 87 | 85 | 90 | 85 | 90 |  | 1,6
| - of which installation (%) | 13 | 13 | 13 | 10 | 15 | 10 | 15 |  | 1,6
| Fixed O&M ($/MWe/year) | 494000 | 309000 | 232000 | 144000 | 845000 | 72000 | 391000 |  | 1,5
Variable O&M ($/MWh)
Start-up costs ($/MWe/start-up)
Technology specific data
References:
1 | Ocean Energy Systems - OES (IEA), “International Levelised Cost of Energy for Ocean Energy Technologies,” 2015.
2 | IRENA, "Wave Energy Technology Brief", 2014
3 | Aderinto and Li, Review on Power Performance and Efficiency of Wave Energy Converters, 2019
4 | Danish Energy Agency, 2012.Technology Data on Energy Plants - Generation of Electricity and District Heating.
5 | Ernst & Young, “Cost of and financial support for wave, tidal stream and tidal range generation in the UK,” 2010.
6 | Carbon Trust, Future Marine Energy, 2010
7 | Intelligent Energy Systems (IES) and Mekong Economics (MKE), Alternatives for Power Generation in the Greater Mekong Sub-Region, 2014
Notes:
A | Many different types of converters and system designs are being researched and tested, and the industry has not converged on a specific design.
B | Number of small units are combined to setup a large wave farm. With time it can be expected to have larger unit sizes and also large wave farm configurations.
C | Depends on the power-take-off system. Many configurations are being explored and that is why there is a wide range.
Note on B32: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: % signs included
Note on I32: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: changed to numbers without %

## 11 Biomass power plant (small)
Technology
| Technology | Biomass power plant (small plant)
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1;5
| Generating capacity for total power plant (MWe) | 25 | 25 | 25 | 1 | 50 | 1 | 50 |  | 1;5
| Electricity efficiency, net (%), name plate | 32 | 32 | 32 | 25 | 35 | 25 | 35 |  | 1;3;7
| Electricity efficiency, net (%), annual average | 31 | 31 | 31 | 25 | 35 | 25 | 35 |  | 1;3;7
| Forced outage (%) | 7 | 7 | 7 | 5.25 | 8.75 | 5.25 | 8.75 | A | 1
| Planned outage (weeks per year) | 6 | 6 | 6 | 4.5 | 7.5 | 4.5 | 7.5 | A | 1
| Technical lifetime (years) | 25 | 25 | 25 | 18.75 | 31.25 | 18.75 | 31.25 | A | 8;7
| Construction time (years) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | A | 7
| Space requirement (1000 m2/MWe) | 35 | 35 | 35 | 26.25 | 43.75 | 26.25 | 43.75 | A | 1;9
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | [5 empty] | 3
| Minimum load (% of full load) | 30 | 30 | 30 | [5 empty] | 3
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | [5 empty] | 3
| Cold start-up time (hours) | 10 | 10 | 10 | [5 empty] | 3
Environment
| PM 2.5 (mg per Nm3) | 12.5 | 12.5 | 12.5 | [5 empty] | 3
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3
Financial data
| Nominal investment (M$/MWe) | 1.7883 | 1.6452 | 1.4306 | 1.3412 | 2.2354 | 1.073 | 1.7883 | B | 4-8;10
| - of which equipment (%) | 65 | 65 | 65 | 50 | 85 | 50 | 85 |  | 1;2
| - of which installation (%) | 35 | 35 | 35 | 15 | 50 | 15 | 50 |  | 1;2
| Fixed O&M ($/MWe/year) | 49500 | 45500 | 39600 | 37100 | 61900 | 29700 | 49500 | A | 4;5;8;10
| Variable O&M ($/MWh) | 3.1638 | 2.9107 | 2.5311 | 2.3729 | 3.9548 | 1.8983 | 3.1638 | A | 5;10
Start-up costs ($/MWe/start-up)
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | ASEAN Centre of Energy, 2016, "Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states".
3 | Danish Energy Agency and COWI, 2017, "Technology catalogue for biomass to energy".
4 | IRENA, 2015, "Renewable power generation cost in 2014"
5 | IFC and BMF, 2017, "Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | India Central Electricity Authority, 2007, "Report on the Land Requirement of Thermal Power Stations".
10 | Learning curve approach for the development of financial parameters.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.
B | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 12 MSW incineration
Technology
| Technology | Incineration Power Plant - Municipal Solid Waste
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 21.5896 | 22.3341 | 23.0786
| Generating capacity for total power plant (MWe) | 21.5896 | 22.3341 | 23.0786
| Electricity efficiency, net (%), name plate | 29 | 30 | 31 | 28 | 32 | 30 | 33 | A | 1
| Electricity efficiency, net (%), annual average | 28 | 29 | 29 | 26 | 30 | 28 | 31 |  | 1
| Forced outage (%) | 1 | 1 | 1 | [5 empty] | 1
| Planned outage (weeks per year) | 2.9 | 2.6 | 2.1 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 1
| Construction time (years) | 2.5 | 2.5 | 2.5 | [5 empty] | 1
| Space requirement (1000 m2/MWe) | 1.5 | 1.5 | 1.5 | [5 empty] | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 10 | 10 | 10 | 7.5 | 12.5 | 7.5 | 12.5 | C | 1
| Minimum load (% of full load) | 20 | 20 | 20 | 15 | 25 | 15 | 25 | C | 1
| Warm start-up time (hours) | 0.5 | 0.5 | 0.5 | 0.375 | 0.625 | 0.375 | 0.625 | C | 1
| Cold start-up time (hours) | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 | C | 1
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 5.6 | 5.2 | 4.6 | 4.1 | 9.3965 | 3.4 | 9.3965 | C | 1
| - of which equipment (%) | 59 | 54 | 50 | - | - | - | - |  | 1
| - of which installation (%) | 41 | 46 | 50 | - | - | - | - |  | 1
| Fixed O&M ($/MWe/year) | 253400 | 233700 | 201200 | 202700 | 316700 | 160900 | 251500 | C | 1
| Variable O&M ($/MWh) | 25.0998 | 24.3052 | 23.4771 | 18.8249 | 29.3464 | 17.6079 | 29.3464 | C | 1
Start-up costs ($/MWe/start-up)
Technology specific data
| Waste treatment capacity (tonnes/h) | 27.7 | 27.7 | 27.7 |  |  |  |  | B
References:
1 | Danish Technology Catalogue “Technology Data for Energy Plants, Danish Energy Agency 2107- update in progress
Notes:
A | Based on experience from the Netherlands where 30 % electric efficiency is achieve. 1 %-point efficiency subtracted to take into account higher temperature of cooling water in Indonesia (approx. +20 C).
B | The investment cost is based on waste to energy CHP plant in Denmark, according to Ref 1. A waste treatment capacity of 27,7 tonnes/h is assumed and an energy content of 10,4 GJ/ton. The specific finalcial data is adjusted to reflect that the plant in Indonesia runs in condensing mode and hence the electric capacity (MWe) is higher than for a combined heat and power, backpressure plant with the same treatment capacity.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Calculated from size, fuel efficiency and an average calory value for waste of 9.7 GJ/ton.
Note on C29: [Trådet kommentar] Din version af Excel lader dig læse denne trådede kommentar. Eventuelle ændringer vil dog blive fjernet, hvis filen åbnes i en nyere version af Excel. Få mere at vide: https://go.microsoft.com/fwlink/?linkid=870924 Kommentar: Revised to be % instead of M$/MWe Besvar: C29 to E30

## 12 Landfill gas
Technology
| Technology | Landfill Gas Power Plant - Municipal Solid Waste
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | 0.5 | 10 | 0.5 | 10 |  | 1
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | 25 | 37 | 25 | 37 |  | 2
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | 25 | 37 | 25 | 37 |  | 2
| Forced outage (%) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Planned outage (weeks per year) | 5 | 5 | 5 | 2 | 15 | 2 | 15 |  | 4
| Technical lifetime (years) | 25 | 25 | 25 | 20 | 30 | 20 | 30 |  | 3
| Construction time (years) | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 |  | 3
Space requirement (1000 m2/MWe)
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.599 | 2.599 | 2.599 | 2.3627 | 2.8589 | 2.3627 | 2.9889 | A | 3
| - of which equipment (%) | 70 | 70 | 70 | 70 | 80 | 70 | 80 |  | 5
| - of which installation (%) | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 5
| Fixed O&M ($/MWe/year) | 130000 | 130000 | 130000 | 118100 | 142900 | 118100 | 149400 | A | 3
Variable O&M ($/MWh)
Start-up costs ($/MWe/start-up)
References:
1 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority, Jakarta, Indonesia
2 | Renewables Academy" (RENAC) AG, 2014, "Biogas Technology and Biomass", Berlin, Germany.
3 | IEA-ETSAP and IRENA, 2015. "Biomass for Heat and Power, Technology Brief".
4 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
5 | MEMR, 2015, "Waste to Energy Guidebook", Jakarta, Indonesia.
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.

## 13 Biogas power plant (small)
Technology
| Technology | Biogas power plant
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Generating capacity for total power plant (MWe) | 1 | 1 | 1 | [5 empty] | 3
| Electricity efficiency, net (%), name plate | 35 | 35 | 35 | [5 empty] | 4
| Electricity efficiency, net (%), annual average | 34 | 34 | 34 | [5 empty] | 4
| Forced outage (%) | 5 | 5 | 5 | [5 empty] | 1
| Planned outage (weeks per year) | 5 | 5 | 5 | [5 empty] | 1
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 7
| Construction time (years) | 1.5 | 1.5 | 1.5 | [5 empty] | 7
| Space requirement (1000 m2/MWe) | 70 | 70 | 70 | [5 empty] | 12
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 20 | 20 | 20 | 10 | 30 | 10 | 30 |  | 11
| Minimum load (% of full load) | 20 | 30 | 15 | 30 | 50 | 10 | 40 |  | 10
Warm start-up time (hours)
Cold start-up time (hours)
Environment
PM 2.5 (mg per Nm3)
SO2 (degree of desulphuring, %)
NOX (g per GJ fuel)
Financial data
| Nominal investment (M$/MWe) | 2.8901 | 2.6589 | 2.3121 | 2.1676 | 3.6126 | 1.7341 | 2.8901 | A | 3;5;8;9
| - of which equipment (%) | 65 | 65 | 65 | 50 | 85 | 50 | 85
| - of which installation (%) | 35 | 35 | 35 | 15 | 50 | 15 | 50
| Fixed O&M ($/MWe/year) | 100800 | 92700 | 80700 | 75700 | 126100 | 60500 | 100800 | A | 5;7;9
| Variable O&M ($/MWh) | 0.11436 | 0.10521 | 0.091485 | 0.085767 | 0.14295 | 0.068614 | 0.11436 | A | 6;9
Start-up costs ($/MWe/start-up)
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | ASEAN Centre of Energy (2016). Levelised cost of electricity generation of selected renewable energy technologies in the ASEAN member states.
3 | Winrock, 2015, "Buku Panduan Konversi POME Menjadi Biogas, Pengembangan Proyek di Indonesia", USAID – Winrock International.
4 | RENAC, 2014, "Biogas Technology and Biomass, Renewables Academy (RENAC)".
5 | IFC and BMF, 2017, Converting biomass to energy - A guide for developmers and investors".
6 | OJK, 2014, "Clean Energy Handbook for Financial Service Institutions", Indonesia Financial Service Authority.
7 | IEA-ETSAP and IRENA, 2015, "Biomass for Heat and Power, Technology Brief".
8 | PKPPIM, 2014, "Analisis biaya dan manfaat pembiayaan investasi limbah menjadi energi melalui kredit program", Center for Climate Change and Multilateral Policy Ministry of Finance Indonesia.
9 | Learning curve approach for the development of financial parameters.
10 | Vuorinen, A., 2008, "Planning of Optimal Power Systems".
11 | Deutsches Institut für Wirtschaftsforschung, On Start-up Costs of Thermal Power Plants in Markets with Increasing Shares of Fluctuating Renewables, 2016.
12 | Chazaro Gerbang Internasional, 2004, "Utilization of Biogas Generated from the Anaerobic Treatment of Palm Oil Mills Effluent (POME) as Indigenous Energy Source for Rural Energy Supply and Electrification - A Pre-Feasibility Study Report"
Notes:
A | Uncertainty (Upper/Lower) is estimated as +/- 25%.

## 14 ICE - Diesel
Technology
| Technology | Internal combustion engine (using fuel oil)
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 20 | 20 | 20 | [5 empty] | 1
| Generating capacity for total power plant (MWe) | 100 | 100 | 100
| Electricity efficiency, net (%), name plate | 46 | 47 | 48 | [5 empty] | 1
| Electricity efficiency, net (%), annual average | 45 | 46 | 47 | 43 | 47 | 45 | 52 |  | 1
| Forced outage (%) | 3 | 3 | 3
| Planned outage (weeks per year) | 0.8 | 1 | 1 | [5 empty] | 2
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 2
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 2
| Space requirement (1000 m2/MWe) | 0.05 | 0.05 | 0.05 | [5 empty] | 2
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 100 | 100 | 100 | [5 empty] | 8;9;10
| Minimum load (% of full load) | 6 | 6 | 6 |  |  |  |  | A | 1;8;9;10
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | [5 empty] | 1;8;9;10
| Cold start-up time (hours) | 0.2 | 0.2 | 0.2 | [5 empty] | 8;9;10
Environment
| PM 2.5 (gram per Nm3) | 19.6 | 19.6 | 19.6 |  |  |  |  | B; C | 3;4
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 |  |  |  |  | C | 3;4
| NOX (g per GJ fuel) | 280 | 280 | 280 |  |  |  |  | C | 3;4
Financial data
| Nominal investment (M$/MWe) | 0.6 | 0.58 | 0.55 | 0.55 | 0.7 | 0.5 | 0.65 | D | 6;7;9;10
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 10000 | 9500 | 9000 | [5 empty] | 2;9;10
| Variable O&M ($/MWh) | 6.5 | 6 | 5.5 | [5 empty] | 2;9;10
| Start-up costs ($/MWe/start-up) | - | - | -
References:
1 | Wärtsila, 2011, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants
2 | Danish Energy Agency, 2016, "Technology Data for Energy Plants"
3 | Minister of Environment, Regulation 21/2008
4 | The International Council on Combustion Engines, 2008: Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2
5 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
6 | BWSC once again to deliver highly efficient power plant in the Faroe Islands.
7 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
8 | IRENA, Flexibility in Conventional Power Plants, 2019. https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2019/Sep/IRENA_Flexibility_in_CPPs_2019
9 | Danish Energy Agency, 2020, "Technology Data - Generation of Electricity and District Heating"
10 | Data delivered by Wartsila, January 2021
Notes:
A | 30 % minimum load per unit - corresponds to 6 % for total plant when consisting of 5 units
B | Total particulate matter
C | Typical diesel exhaut emission according to Ref 3 (average of interval) unless this number exceeds the maximum allowed emission according to Minister of Environment Regulation 21/2008. Both SO2 and particulates are dependant on the fuel composition.
D | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 14 ICE - natural gas
Technology
| Technology | Internal combustion engine (using natural gas)
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 20 | 20 | 20 | [5 empty] | 1
| Generating capacity for total power plant (MWe) | 100 | 100 | 100
| Electricity efficiency, net (%), name plate | 47 | 48 | 49 | [5 empty] | 1;9;10
| Electricity efficiency, net (%), annual average | 46 | 47 | 48 | 44 | 48 | 46 | 52 |  | 1;9;10
| Forced outage (%) | 3 | 3 | 3
| Planned outage (weeks per year) | 0.8 | 1 | 1 | [5 empty] | 2
| Technical lifetime (years) | 25 | 25 | 25 | [5 empty] | 2
| Construction time (years) | 1 | 1 | 1 | [5 empty] | 2
| Space requirement (1000 m2/MWe) | 0.05 | 0.05 | 0.05 | [5 empty] | 2
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | -
| Capacity factor (%), incl. outages | - | - | -
Ramping configurations
| Ramping (% per minute) | 100 | 100 | 100 | [5 empty] | 8;9;10
| Minimum load (% of full load) | 6 | 6 | 6 |  |  |  |  | A | 1;8;9;10
| Warm start-up time (hours) | 0.05 | 0.05 | 0.05 | [5 empty] | 1;8;9;10
| Cold start-up time (hours) | 0.2 | 0.2 | 0.2 | [5 empty] | 8;9;10
Environment
| PM 2.5 (gram per Nm3) | 7.5 | 7.5 | 7.5 |  |  |  |  | B | 3;4;9;10
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | [5 empty] | 3;4
| NOX (g per GJ fuel) | 125 | 125 | 125 | [5 empty] | 3;4;9;10
Financial data
| Nominal investment (M$/MWe) | 0.6 | 0.58 | 0.55 | 0.55 | 0.7 | 0.5 | 0.65 | C | 6;7;9;10
- of which equipment (%)
- of which installation (%)
| Fixed O&M ($/MWe/year) | 10000 | 9500 | 9000 | [5 empty] | 2;9;10
| Variable O&M ($/MWh) | 6.5 | 6 | 5.5 | [5 empty] | 2;9;10
| Start-up costs ($/MWe/start-up) | - | - | -
References:
1 | Wärtsila, 2011, "White paper Combustion engine power plants", Niklas Haga, General Manager, Marketing & Business Development Power Plants
2 | Danish Energy Agency, 2016, "Technology Data for Energy Plants"
3 | Minister of Environment, Regulation 21/2008
4 | The International Council on Combustion Engines, 2008: Guide to diesel exhaust emissions control of NOx, SOx, particles, smoke and CO2
5 | http://www.bwsc.com/News---Press.aspx?ID=530&PID=2281&Action=1&NewsId=206
6 | BWSC once again to deliver highly efficient power plant in the Faroe Islands.
7 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
8 | IRENA, Flexibility in Conventional Power Plants, 2019. https://www.irena.org/-/media/Files/IRENA/Agency/Publication/2019/Sep/IRENA_Flexibility_in_CPPs_2019
9 | Danish Energy Agency, 2020, "Technology Data - Generation of Electricity and District Heating"
10 | Data delivered by Wartsila, January 2021
Notes:
A | 30 % minimum load per unit - corresponds to 6 % for total plant when consisting of 5 units
B | Total particulate matter
C | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 15 Geothermal - small
Technology
| Technology | Geothermal power plant - small system (binary or condensing)
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 10 | 10 | 10 | 0.3 | 20 | 0.3 | 20 |  | 1;8
| Generating capacity for total power plant (MWe) | 20 | 20 | 20 | 5 | 30 | 5 | 30 |  | 1
| Electricity efficiency, net (%), name plate | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Electricity efficiency, net (%), annual average | 10 | 11 | 12 | 6 | 12 | 8 | 14 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
| Construction time (years) | 2 | 2 | 2 | 1.5 | 3 | 1.5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 30 | 31 | 32 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
Ramping (% per minute)
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | B | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | B | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | B | 6
Financial data
| Nominal investment (M$/MWe) | 4.7042 | 4.3514 | 3.975 | 3.5281 | 5.8802 | 2.9813 | 4.9688 | C;D;E | 1;2;4;8
| - of which equipment (%) | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 3
| - of which installation (%) | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 3
| Fixed O&M ($/MWe/year) | 20800 | 19200 | 17600 | 15600 | 26000 | 13200 | 21900 | C;D | 1;4
| Variable O&M ($/MWh) | 0.38465 | 0.3558 | 0.32503 | 0.28849 | 0.48081 | 0.24377 | 0.40629 | C;D | 1;4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
| Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Budisulistyo & Krumdieck , 2014, "Thermodynamic and economic analysis for the pre- feasibility study of a binary geothermal power plant"
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Climate Policy Initiative, 2015, Using Private Finance to Accelerate Geothermal Deployment: Sarulla Geothermal Power Plant, Indonesia.
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These smaller units are assumed to be binary units at medium source temperatures.
B | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
C | Uncertainty (Upper/Lower) is estimated as +/- 25%.
D | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 15 Geothermal - large
Technology
| Technology | Geothermal power plant - large system (flash or dry)
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 55 | 55 | 55 | 30 | 500 | 30 | 500 |  | 1
| Generating capacity for total power plant (MWe) | 110 | 110 | 110 | 30 | 500 | 30 | 500 |  | 1
| Electricity efficiency, net (%), name plate | 16 | 17 | 18 | 8 | 18 | 10 | 20 | A | 5
| Electricity efficiency, net (%), annual average | 15 | 16 | 17 | 8 | 18 | 10 | 20 | A | 5
| Forced outage (%) | 10 | 10 | 10 | 5 | 30 | 5 | 30 |  | 1
| Planned outage (weeks per year) | 4 | 4 | 4 | 2 | 6 | 2 | 6 |  | 1
| Technical lifetime (years) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 1
| Construction time (years) | 2 | 2 | 2 | 1,5 | 3 | 1,5 | 3 |  | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 20 | 40 | 20 | 40 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | 90 | 90 | 90 | 70 | 100 | 70 | 100 |  | 1
| Capacity factor (%), incl. outages | 80 | 80 | 80 | 70 | 100 | 70 | 100 |  | 1
Ramping configurations
| Ramping (% per minute) | 3 | 10 | 20 | [5 empty] | 8
Minimum load (% of full load)
Warm start-up time (hours)
Cold start-up time (hours)
Environment
| PM 2.5 (gram per Nm3) | - | - | - | - | - | - | - | C | 6
| SO2 (degree of desulphuring, %) | - | - | - | - | - | - | - | C | 6
| NOX (g per GJ fuel) | - | - | - | - | - | - | - | C | 6
Financial data
| Nominal investment (M$/MWe) | 3.6282 | 3.3561 | 3.0658 | 2.7212 | 4.5353 | 2.2994 | 3.8323 | B;D;E | 1;2;3;4
| - of which equipment (%) | 60 | 60 | 60 | 40 | 70 | 40 | 70 |  | 3
| - of which installation (%) | 40 | 40 | 40 | 30 | 50 | 30 | 50 |  | 3
| Fixed O&M ($/MWe/year) | 18700 | 17400 | 15800 | 14000 | 23400 | 11900 | 19800 | B;D | 1;4
| Variable O&M ($/MWh) | 0.2599 | 0.24041 | 0.21962 | 0.19493 | 0.32488 | 0.16471 | 0.27452 | B;D | 1;4
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Exploration costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
| Confirmation costs (M$/MWe) | 0.15 | 0.15 | 0.15 | 0.1 | 0.2 | 0.1 | 0.2 |  | 7
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | IEA, World Energy Outlook, 2015.
3 | IRENA, 2015, Renewable Power Generation Costs in 2014.
4 | Learning curve approach for the development of financial parameters.
5 | Moon & Zarrouk, 2012, “Efficiency Of Geothermal Power Plants: A Worldwide Review”.
6 | Yuniarto, et. al., 2015. “Geothermal Power Plant Emissions in Indonesia”.
7 | Geothermal Energy Association, 2006, "A Handbook on the Externalities, Employment, and Economics of Geothermal Energy".
8 | Geothermal Energy Association, 2015, "Geothermal Energy Association Issue Brief: Firm and Flexible Power Services Available from Geothermal Facilities"
Notes:
A | The efficiency is the thermal efficiency - meaning the utilization of heat from the ground. Since the geothermal heat is renewable and considered free, then an increase in effciency will give a lower investment cost per MW. These large units are assumed to be flach units at high source temperatures.
B | Uncertainty (Upper/Lower) is estimated as +/- 25%, which is an estimate build upon cases from IRENA (ref. 3)
C | Geothermal do emit H2S. From Minister of Environment Regulation 21/2008 this shall be below 35 mg/Nm3.
D | The learning rate is assumed to impact the geothermal specific equipment and installation. The power plant units (i.e. the turbine and pump) is assumed to have very litle development. From Ref. 3 it is assumed that half of the investment cost are on the geothermal specific equipment.
E | Investment cost are including Exploration and Confirmation costs (see under Technology specific data).

## 16 Hydro pumped storage
Technology
| Technology | Hydro pumped storage
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Generating capacity for one unit (MWe) | 250 | 250 | 250 | 100 | 500 | 100 | 500 | A | 1;6
| Generating capacity for total power plant (MWe) | 1000 | 1000 | 1000 | 100 | 4000 | 100 | 4000 |  | 1;6
| Electricity efficiency, net (%), name plate | 80 | 80 | 80 | 70 | 82 | 70 | 82 |  | 1;3;5
| Electricity efficiency, net (%), annual average | 80 | 80 | 80 | 70 | 82 | 70 | 82 |  | 1;3;5
| Forced outage (%) | 4 | 4 | 4 | 2 | 7 | 2 | 7 |  | 5
| Planned outage (weeks per year) | 3 | 3 | 3 | 2 | 6 | 2 | 6 |  | 5
| Technical lifetime (years) | 50 | 50 | 50 | 40 | 90 | 40 | 90 |  | 1
| Construction time (years) | 4.3 | 4.3 | 4.3 | 2.15 | 6.45 | 2.15 | 6.45 | B | 1
| Space requirement (1000 m2/MWe) | 30 | 30 | 30 | 15 | 45 | 15 | 45 |  | 1
Additional data for non thermal plants
| Capacity factor (%), theoretical | - | - | - | - | - | - | -
| Capacity factor (%), incl. outages | - | - | - | - | - | - | -
Ramping configurations
| Ramping (% per minute) | 50 | 50 | 50 | 10 | 100 | 10 | 100 |  | 2;5
| Minimum load (% of full load) | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2
| Warm start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
| Cold start-up time (hours) | 0.1 | 0.1 | 0.1 | 0 | 0.3 | 0 | 0.3 |  | 2
Environment
| PM 2.5 (gram per Nm3) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SO2 (degree of desulphuring, %) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX (g per GJ fuel) | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (M$19/MWe) | 0.89 | 0.89 | 0.89 | 0.6 | 6 | 0.6 | 6 | C;E | 1;3;4
| - of which equipment (%) | 30 | 30 | 30 | 20 | 50 | 20 | 50 |  | 7
| - of which installation (%) | 70 | 70 | 70 | 50 | 80 | 50 | 80 |  | 7
| Fixed O&M ($19/MWe/year) | 8320 | 8320 | 8320 | 4000 | 30000 | 4000 | 30000 |  | 3;4;6.7
| Variable O&M ($19/MWh) | 1.4 | 1.4 | 1.4 | 0.5 | 3 | 0.5 | 3 |  | 1;7
| Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | -
Technology specific data
| Size of reservoir (MWh) | 10000 | 10000 | 10000 | 3000 | 20000 | 3000 | 20000 | D | 1;6
| Load/unload time (hours) | 10 | 10 | 10 | 4 | 12 | 4 | 12 | D | 1;6
References:
1 | Ea Energy Analyses and Danish Energy Agency, 2017, "Technology Data for the Indonesian Power Sector - Catalogue for Generation and Storage of Electricity"
2 | Eurelectric, 2015, "Hydropower - Supporting a power system in transition".
3 | Lazard, 2016, “Lazard’s Levelised Cost of Storage – version 2.0”.
4 | MWH, 2009, Technical Analysis of Pumped Storage and Integration with Wind Power in the Pacific Northwest
5 | U.S. Department of Energy, 2015, “Hydropower Market Report”.
6 | Connolly, 2009, "A Review of Energy Storage Technologies - For the integration of fluctuating renewable energy".
7 | IRENA, 2012, "Renewable Energy Technologies: Cost Analysis Series - Hydropower".
Notes:
A | Size per turbine.
B | Uncertainty (Upper/Lower) is estimated as +/- 50%.
C | Numbers are very site sensitive. There will be an improvement by learning curve development, but this improvement will equalized because the best locations will be utilized first. The investment largely depends on civil work.
D | The size of the total power plant and not per unit (turbine).
E | Investment cost include the engineering, procurement and construction (EPC) cost. See description under Methodology.

## 17 Batteries
Technology
| Technology | Batteries - Lithium-ion (utility-scale)
| US$2019 | 2020 | 2030 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
| Energy/technical data |  |  |  | Lower | Upper | Lower | Upper
| Energy storage capacity for one unit (MWh) | 6 | 7 | 8 |  |  |  |  | A,B | 1,2
| Energy/Power ratio (hours) | 1.04 | 2.08 | 4.163 |  |  |  |  | E | 1,2
| Discharge time (hours) | 0.9984 | 1.9968 | 3.9965 |  |  |  |  | E | 1,2
| Round-trip efficiency (%) AC | 91 | 92 | 92 |  |  |  |  | C | 3,12
| Round-trip efficiency (%) DC | 95 | 96 | 96 |  |  |  |  | C | 3,12
| Self-discharge rate (%/day) | 0.1 | 0.1 | 0.1 | [5 empty] | 4
| Forced outage (%) | 0.38 | 0.35 | 0.25 |  |  |  |  | M
| Planned outage (weeks per year) | 0.2 | 0.1 | 0.1 |  |  |  |  | L
| Technical lifetime (cycles) | 10000 | 15000 | 20000 |  |  |  |  | M | 5
| Technical lifetime (years) | 20 | 25 | 30 |  |  |  |  | D
| Construction time (years) | 0.2 | 0.2 | 0.2
| Energy density (Wh/kg) | 150 | 200 | 300
Ramping configurations
| Response time from idle to full-rated discharge (ms) | 50 | 50 | 50 | [5 empty] | 6
Financial data
| Nominal investment (MUSD/MWh) | 0.5785 | 0.26415 | 0.15727 | 0.45502 | 0.92032 | 0.075043 | 0.39799 | G | 13
| - energy component (MUSD/MWh) | 0.152 | 0.062 | 0.035 | 0.079552 | 0.21479 | 0.029548 | 0.13069 |  | 7,8
| - power component (MUSD/MW) | 0.311 | 0.184 | 0.069 | 0.27275 | 0.57959 | 0.045458 | 0.28411 | H | 9,10,11
| - other project costs (MUSD/MWh) | 0.115 | 0.11 | 0.105 | 0.10228 | 0.12501 | 0.022729 | 0.12501 | N | 9,12
| Fixed O&M (USD/MWh/year) | 621 | 310.5 | 155.1381 | 500 | 650 | 250 | 350 |  | 12
| Variable O&M (USD/MWh) | 2.3 | 2.07 | 1.84 | 0.45458 | 6.3642 | 0.34094 | 2.8411 | I | 10
Technology specific data
| Energy storage expansion cost (MUSD/MWh) | 0.267 | 0.163 | 0.086 | 0.18183 | 0.29434 | 0.052277 | 0.20002 | B,F | 7,8
| Output capacity expansion cost (MUSD/MW) | 0.311 | 0.184 | 0.069 | 0.27275 | 0.57959 | 0.045458 | 0.28411 | B,F | 9,10,11
References:
1 | Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
2 | Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
3 | L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
4 | Fan Xiayue, "Battery technologies for grid-level large-scale electrical energy storage", Transactions of Tianjin University, Springer, 2020.
5 | Environmental end energy study institute, Energy storage factsheet, https://www.eesi.org/papers/view/energy-storage-2019.
6 | D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127.
7 | Bloomberg New Energy Finance. New Energy Outlook 2019, 2019.
8 | International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
9 | R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17.
10 | B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596.
11 | G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015).
12 | Lazard, Lazard's Levelized Cost of Storage (2019).
13 | IEA, World Energy Outlook 2019, 2019.
Notes:
A | One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [2,14]. Units with C-rates below/above 1 are possible, depending on the system needs and cost of the energy and power rating components. A C-rate of 1 is here assumed for 2020, as it is close to several new installations.
B | Power and energy output can be scaled linearly by utilizing many modules (up to 100MW has been demonstrated). Output capacity expansion can be done reprogramming the management unit without any new battery module.
C | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D | Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C. Steady improvement in battery lifetime due to better materials and battery management expected. Number of cycles can be a more meaningful lifetime indicator.
E | The discharge time is the amount of hours the battery can discharge at rated output capacity. It equals the Energy/Power ratio corrected for the discharge efficiency.
F | Since multi-MWh LIB systems are scalar, the energy and outputr capacity expansion costs are here estimated to be equal to the energy and output capacity components plus the “other costs”
G | Power conversion cost is strongly dependent on scalability and application.
H | The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
I | Cost per MWh of energy discharged from the battery
L | It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
M | Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
N | Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards.